## Agenda and Attendees
Yuri 30% Design Review (PV/BESS)
Date | 2022-09-07
Attendees
1 | Daniele Perretta, OE PM, Tractebel Engie
2 | Phil Harford, Engie, Project Manager
3 | Filippe Rimis - Project Engineer - Technip Energies
4 | Swannie Swanepoel - PSD Energy - Project Lead
5 | Theo Sonnenberg - PSD Energy, Senior Primary Designer
6 | Andreas Merk - Technical PM - Engie
7 | Lucas Foster - Construction & Commissioning Lead - T.EN
8 | Damien Amigues, T.EN, PM
9 | Ahmed Tayeh -PSD Energy, Senior PV Engineer.
10 | Kapil Tare -Structural Lead T.EN MOC
11 | Baalu Veluswamy - Process/Project Engineer YCA
12 | Tayah Thornton - WHSE Manager MFG
13 | Sanjay Mone Sr Control System Engineer Technip AOC
14 | Michael Vosfeld - Monford Superintendant
15 | Ivan Patchel, Monford, O&M Manager
16 | Brian Rafferty, COO, Monford
17 | Brian Howarth = Project Director, Yara
18 | Kinley Dorji, Civil Engineer, Monford
19 | Anthony Abraham, Engineeirng Manager, TEN
20 | Duncan Zajdlewicz
21 | Viralkumar Raval

## Actions
Yuri 30% Design Review (PV/BESS)
Date - 07 Sept 2022
Item No. | Discipline | Description | Action/Note
1 | Structural | Footbridges to walk over the piperacks. This is mainly at the back of the H2 Plant. To be covered in HAZID. | Action
2 | Electrical | What is the access width for O&M if the Combiner Box protrudes at the back of the Panels? | Action
3 | Civil | Delineate new vs existing fences on drawings. Include access gates within the layout. | Action
4 | Electrical | Acceptable if robotic cleaning used. If tractor is proposed than single access to each row will not be acceptable. | Note
5 | Electrical | Is one Cloud Monitoring System is sufficient or not, can we please check with OEM. | Action
6 | Electrical | The RMU Breakers are manual. The system is not self healing. | Note
7 | Electrical | Sungrow BESS - Safety Checklist Spreadsheet | Action
8 | Electrical | EMS Workshops to be arranged. Long term and Short term weather data incorporation. Will the EMS incorporate this? | Action
9 | Electrical | Clarification of 5MW Swing for the Yuri Project. Engie to provide Clarification. | Action
10 | Electrical | Is there a VPN into SCADA Connection? | Action
11 | Electrical | What if we want to change the EMS Logic. Is there a Service Level Agreement that will facilitate this? | Action
12 | Electrical | Forecast Weather Data. Who will be procuring this information. How will this information flow. | Action
13
14
15
16
17
18
19
20

## List
Disciplines | Action/Note
Electrical | Action
Civil | Note
Structural